## 1. CAEMS IQ-OQ Commissioning
FIELD INSTALLATION REPORT COMMISSIONING REPORT
IQ-Installation Qualification
OQ – Operational Qualification
Compressed Air Solution provider: | Company address: |  | CAEMS:
Location name:
Contact person:
PROJECT:
This Installation Qualification Protocol (IQ) for the CAEMS outlines the responsibilities and activities to be accomplished to qualify the CAEMS
according to the requirements of customer.
The Installation Qualification Protocol should be completed before an Operation Qualification Assessment is made.
| Name | Signature | Date
Test prepared by
The undersigned persons confirm that IQ OQ verification tests are accepted and done according to documentation.
We confirm that the test is properly prepared.
Company | Name | Signature | Date
TEST PURPOSE
The purpose of the IQ-OQ test is to test input / output signals on the controller (PLC) and to verify the compliance of the electrical connections of the points
to input and output modules to the controller.
This involves visually checking the effect signal to the process actuators and meassuring equipment (e.g. Compressors, Pressure transmitters, flow meters ...)
Testing is carried out via tables with input and output signals with connection to CAEMS application.
As qualification considering the proper conversion of the analog signal processing in the grandeur of the analog input signal,
converting software size of the process in analog outputs, proper detection of the state of the digital inputs and trigger appropriate action at the digital output.
| Name | Signiture | Date
Tested by
Verified by
The project was successfully carried out with all qualifying tests as follows:
Test | Test |  | Remarks
| From - To | Tested / Signiture
IQ IO PLC – Input/output signal and wiring test
IQ HDS – CAEMS System Hardware Test
IQ TAB HMI PLC – HMI Data test
IQ SDS – CAEMS Cloud System Application test
OQ FNS PLC – CAEMS Control system Function Test
Status of CAEMS system upon completion of qualification (IQ, OQ):
1. The CAEMS system operates in accordance with the functional specification ( FS )
2. Hardware and Software system equipment are in accordance with HDS and SDS
3. The CAEMS system is ready for use in the production
| Name | Date | Signature
Report created by
Tested by
Verified by
Approved by

## 2. CAEMS Installation Setup
CAEMS CS-2-4-8-CFC Field Installation Setup IQ-OQ
Compressed Air Solution Provider |  |  |  |  | Company:
Address:
Location name: Location address:
[5 empty] | Tel: |  | Email:
Date: |  | 2018-01-15 07:42 |  |  | Technical Person:
| CAEMS Type |  |  | CAEMS SN:
| CS MAC Address: |  |  | VPN IP address:
| Currency | EUR
| Electricity Cost | 0.08 | Currency/kWh
| Compressed Air Cost | 0.025 | Currency/m3
COMPRESSED AIR SYSTEM DETAILS:
Target specific power
Pressure setpoint
Pressure max (unload)
Pressure min (load)
Pressure min critical
Take picture of each compressor Nameplate and CAEMS:
| Voltage 3F measurment: |  | V
Compressor Data:
|  | C.01 | C.02 | C.03 | C.04 | C.05 | C.07 | C.07 | C.08
Name
Year of manufacture
Type (on/off,VSD)
Nominal Capacity(m3/min)
Nominal Pressure(bar)
Nominal Power(kW)
Dryer (YES,NO)
Cooling (AIR,WATER)
cos fi
Service Factor -motor
Working hours
IP Address
1 | IQ IO PLC – Input/output signal and wiring test
TAGs:
| Analog inputs | Electrical terminals | Compressor Link | Label Type | Label | Unit | Description | Range | Tested/ Signature
|  |  | Signal linked to compressor: C.01, C.02, C.03, C.04 or - | Flow, Pressure, Power, Vibration, Ultrasound, Temperature | Total Flow, Total Pressure, Total Power, Custom | barg, kPa, m3/min, cfm, kW ... |  | 4-20 mA --> Use physical units
| AI1 | C.01: AI1.I1
| AI2 | C.01: AI1.I2
| AI3 | C.01: AI1.I3
| AI4 | C.01: AI1.I4
| AI5 | C.01: AI2.I1
| AI6 | C.01: AI2.I2
| AI7 | C.01: AI2.I3
| AI8 | C.01: AI2.I4
| AI17 | C.02: MRV1; C.03: Position signal; C.05: %; C.07: 0-100%
| AI18 | C.02: BRV1; C.03: Position signal; C.05: %; C.07: 0-100%
| AI21 |  | - | Custom | Calc AIR FLOW | m3/min | Calculated AIR FLOW | 0-500
| Analog outputs | Electrical terminals | Compressor Link |  |  |  | Description | Range | Tested/ Signature
|  |  | Signal linked to compressor: C.01, C.02, C.03, C.04 or - |  |  |  | Remote pressure, %VSD CFC MRV1, CFC BRV1 | 4-12-20 mA --> 0-50-100% 0-5-10V
| AO1 | C.01: AO1.O1; C.02: C.01
| AO2 | C.01: AO1.O2; C.02: C.01
| AO3 | C.01: AO2.O1; C.02: C.02
| AO4 | C.01: AO2.O2; C.02: C.02
| AO5 | C.01: AO3.O1; C.02: C.03
| AO6 | C.01: AO3.O2; C.02: C.03
| AO7 | C.01: AO4.O1; C.02: C.04
| AO8 | C.01: AO4.O2; C.02: C.04
| AO9 | C.01: AO5.O2; C.02: C.05
| AO10 | C.01: AO5.O2; C.02: C.05
| AO11 | C.01: AO6.O1; C.02: C.06
| AO12 | C.01: AO6.O2; C.02: C.06
| AO13 | C.01: AO7.O1; C.02: C.07
| AO14 | C.01: AO7.O2; C.02: C.07
| AO15 | C.01: AO8.O1; C.02: C.08
| AO16 | C.01: AO8.O2; C.02: C.08
| AO17 | C.01: AO.O1; C.02: CS-Box
| AO18 | C.01: AO.O2; C.02: CS-Box
| Analog Power inputs AIP | Electrical terminals | Compressor Link | Label Type | Label | Unit | Description | Range | Tested/ Signature
|  |  | Signal linked to compressor: C.01, C.02, C.03, C.04 or - | Power | Power | kW |  | CT x/ A
| AIP1 | C.01: AIP.01; C.02: C.01
| AIP2 | C.01: AIP.02; C.02: C.02
| AIP3 | C.01: AIP.03; C.02: C.03
| AIP4 | C.01: AIP.04; C.02: C.04
| AIP5 | C.01: AIP.05; C.02: C.05
| AIP6 | C.01: AIP.06; C.02: C.06
| AIP7 | C.01: AIP.07; C.02: C.07
| AIP8 | C.01: AIP.08; C.02: C.08
| Digital inputs | Electrical terminals | Compressor Link | Label Type | Label | Description | DI Type |  | Tested/ Signature
|  |  | Signal linked to compressor: C.01, C.02, C.03, C.04 or - | Digital State | C. working C. Loaded C. Alarm Custom |  | NO/NC
| DI1 | C.01: DI.00.01; C.02: CS-BASE
| DI2 | C.01: DI.00.02; C.02: CS-BASE
| DI3 | C.01: DI.00.03; C.02: CS-BASE
| DI4 | C.01: DI.00.04; C.02: CS-BASE; C.03: internaly used
| DI5 | C.01: DI.00.05; C.02: CS-BASE
| DI6 | C.01: DI.00.06; C.02: CS-BASE
| DI7 | C.01: DI.00.07; C.02: CS-BASE
| DI8 | C.01: DI.00.08; C.02: CS-BASE
| DI9 | C.01: DI.01.01; C.02: C.01; C.03: Digital state; C.04: C. Working
| DI10 | C.01: DI.01.02; C.02: C.01; C.03: Digital state; C.04: C.Loaded
| DI11 | C.01: DI.01.03; C.02: C.01; C.03: Digital state; C.04: C.Alarm
| DI12 | C.01: DI.01.04; C.02: C.01; C.04: Remote*
| DI13 | C.01: DI.02.01; C.02: C.02; C.03: Digital state; C.04: C. Working
| DI14 | C.01: DI.02.02; C.02: C.02; C.03: Digital state; C.04: C.Loaded
| DI15 | C.01: DI.02.03; C.02: C.02; C.03: Digital state; C.04: C.Alarm
| DI16 | C.01: DI.02.04; C.02: C.02; C.04: Remote*
| DI17 | C.01: DI.03.01; C.02: C.03; C.03: Digital state; C.04: C. Working
| DI18 | C.01: DI.03.02; C.02: C.03; C.03: Digital state; C.04: C.Loaded
| DI19 | C.01: DI.03.03; C.02: C.03; C.03: Digital state; C.04: C.Alarm
| DI20 | C.01: DI.03.04; C.02: C.03; C.04: Remote*
| DI21 | C.01: DI.04.01; C.02: C.04; C.03: Digital state; C.04: C. Working
| DI22 | C.01: DI.04.02; C.02: C.04; C.03: Digital state; C.04: C.Loaded
| DI23 | C.01: DI.04.03; C.02: C.04; C.03: Digital state; C.04: C.Alarm
| DI24 | C.01: DI.04.04; C.02: C.04; C.04: Remote*
| DI25 | C.01: DI.05.01; C.02: C.05; C.03: Digital state; C.04: C. Working
| DI26 | C.01: DI.05.02; C.02: C.05; C.03: Digital state; C.04: C.Loaded
| DI27 | C.01: DI.05.03; C.02: C.05; C.03: Digital state; C.04: C.Alarm
| DI28 | C.01: DI.05.04; C.02: C.05; C.04: Remote*
| DI29 | C.01: DI.06.01; C.02: C.06; C.03: Digital state; C.04: C. Working
| DI30 | C.01: DI.06.02; C.02: C.06; C.03: Digital state; C.04: C.Loaded
| DI31 | C.01: DI.06.03; C.02: C.06; C.03: Digital state; C.04: C.Alarm
| DI32 | C.01: DI.06.04; C.02: C.06; C.04: Remote*
| DI33 | C.01: DI.07.01; C.02: C.07; C.03: Digital state; C.04: C. Working
| DI34 | C.01: DI.07.02; C.02: C.07; C.03: Digital state; C.04: C.Loaded
| DI35 | C.01: DI.07.03; C.02: C.07; C.03: Digital state; C.04: C.Alarm
| DI36 | C.01: DI.07.04; C.02: C.07; C.04: Remote*
| DI37 | C.01: DI.08.01; C.02: C.08; C.03: Digital state; C.04: C. Working
| DI38 | C.01: DI.08.02; C.02: C.08; C.03: Digital state; C.04: C.Loaded
| DI39 | C.01: DI.08.03; C.02: C.08; C.03: Digital state; C.04: C.Alarm
| DI40 | C.01: DI.08.04; C.02: C.08; C.04: Remote*
| DI41 | C.02: CFC; C.03: Digital state; C.04: BRV1 Opened; C.07: NO
| Calculations | Compressor Link | Label Type | Label | Unit | Formula | Description |  | Tested/ Signature
|  | Signal linked to compressor: C.01, C.02, C.03, C.04 or - | Flow, Pressure, Power, Vibration, Ultrasound, Temperature | Total Flow, Total Pressure, Total Power, Specific Power, Custom | barg, kPa, m3/min, cfm, kW ... | you can use any formula with AI l. E: AI1/AI2
| CI1 | C.01: Total Power
| CI2 | C.01: Total Flow
| CI3 | C.01: Total Specific Power
CI4
CI5
CI6
CI7
CI8
CI9
CI10
WARNINGS
Recepients (E-mail) | bar: C.01 to C.04
| Input signal | C.01: Trigger; C.02: Value; C.03: Description; C.04: Tested / Signature
ALARMS
Recepients (Email) | bar: C.01 to C.04
| Input signal | C.01: Trigger; C.02: Value; C.03: Description; C.04: Tested / Signature
DI11-Compressor1 Alarm | bar: C.01
DI15-Compressor2 Alarm | bar: C.01
DI19-Compressor3 Alarm | bar: C.01
DI23-Compressor4 Alarm | bar: C.01
DI27-Compressor5 Alarm | bar: C.01
DI31-Compressor6 Alarm | bar: C.01
DI35-Compressor7 Alarm | bar: C.01
DI39-Compressor8 Alarm | bar: C.01
2. | IQ HDS – CAEMS System Hardware Test
CAEMS CS-4 system configuration
Pos | PN | C.01: Description; C.03: SN; C.04: Qty; C.05: Checked/ Signature
1 | CS-BASE | C.01: CS-4 BASE unit
2 | OP-HMI4.3 Eth | C.01: Operator panel HMI 4.3
3 | CS-3G-LAN | C.01: Cellular GSM modem 3G Router
4 | CS-LAN | C.01: LAN Router
Measurement Equipment | bar: C.01 to C.05
1 | Flowmeter | C.01: FCI FS10A 024412
2 | Pressure transmitter | C.01: Baumer 16bar
3 | Current transmitter | C.01: CT500/4-20mA
4 | Current transmitter | C.01: CT 300/5A
5 | Cable | C.01: Cable for measurements
6 | Box | C.01: Box for accessories
7 | Current transmitter | C.01: CT300/4-20mA
HDS test
Criterion
|  | Complies | Date | Signature | Remarks
PLC electro cabinet fits order agreements
Electro scheme documentation complies with actual cabinet state.
All system elements are connected properly to PLC cabinet and to all input-output modules and work properly.
3. | IQ TAB HMI PLC – HMI Data test
CS-4 box PLC configuration check
| Description | C.02: Checked by; C.03: Signature
CAEMS CS PLC configuration
CS Control box circuit breaker switch
Criterion | bar: C.01 to C.05
|  |  | Comply | Date | Signature | Remarks
CS box is connected to power supply and to internet and communication is live and system is online
Compressed air system data and compressed air equipment data are entered in CS HMI
All signals: AIs, AIPs, DIs are setup correctly, meassuring ranges are set and values on HMI and instrumentation are the same
All pages of HMI are checked and working correctly
EtherCAT communication CS and CS-C-on-off or VSD modules is working AIPS are tested
EMCS Control System is enabled, parameters are set *
CFC- CAEMS Flow Controller is set and tested. Regulation range of CFC is manualy tested 0-100%. *
Control and monitoring software app works correctly and adequately respond to changes in the system, according to the specifications given in the FS functional specifications.
Options*
4. | IQ SDS – CAEMS Cloud System Application test
Criterion | bar: C.01 to C.05
|  |  | Comply | Date | Signature | Remarks
CAEMS cloud application is connected to CS box, communication is live and system is online
Remote service VPN connection with CS box is online and working.
Compressed air system data and compressed air equipment data are entered in CAEMS application
Calculated signals Cis (Total Pressure, Total Power, Total Flow and Total Specific power) are entered in CAEMS application.
All signals: AIs, AIPs, DIs are setup correctly, meassuring ranges are set and values on HMI and CAEMS are the same
Warnings and Alarms are set correctly with receivers emails and tested
PI&D of Compressed Air System received and setup on CAEMS app
Analysis log, Alarm detail log and IMOP for each compressor received to CAEMS app from CS-4 box
Remote scada with VNC connection from HMI to CAEMS is connected and working correctly
5 | OQ FNS PLC – CAEMS Control system Function Test | bar: C.01 to C.07
CAEMS monitoring functionality tests
Num. | Status | Signal description | Result | Date | Signature 1 | Signature 2 | Test passed
1 | IMOP function is enabled. | C.01: Compressor is started.; C.02: IMOP file is uploaded on CAEMS.
2 | Force Alarm Log function is enabled. | C.01: /; C.02: Alarm log file is uploaded..
3 | Compressors states are uploaded on CAEMS. | C.01: /; C.02: States on CAEMS and HMI must be the same.
4 | AI inputs are connected and on HMI are selected as used. | C.01: Disconnect one of the AI input.; C.02: After 1 minute "AIProbe" alarm is triggered.
CAEMS EMCS functionality tests
Num. | Compressor status | Signal description | Result | Date | Signature 1 | Signature 2 | Test passed
1 | Compressors are in LOCAL/REMOTE state. | C.01: EMCS is disabled.; C.02: Pressure drops below critical limit. No additional compressor is started.
2 | Compressors are in LOCAL state. | C.01: EMCS is enabled.; C.02: Pressure drops below critical limit. No additional compressor is started.
3 | Compressors are in REMOTE state. | C.01: EMCS is enabled.; C.02: Pressure drops below critical limit. Additional compressor is started by priority.
4 | Compressors are in REMOTE state. | C.01: EMCS is enabled.; C.02: Pressure rises above (setpoint + pressure difference). After setted time compressor is stopped by priority.
5 | Compressors are in REMOTE state. | C.01: Change the priorities.; C.02: PLC starts with priority rotation.
6 | Compressors are in REMOTE state. | C.01: EMCS is enabled.Compressors are in ALARM.; C.02: PLC does not start any compressor.
7 | VFD compressors are in REMOTE state. | C.01: EMCS is enabled. Remote pressure is enabled.; C.02: Compressors are regulating through "remote pressure".
CAEMS CFC functionality tests*
Num. | Status | Signal description | Result | Date | Signature 1 | Signature 2 | Test passed
1 | CFC is in MANUAL mode and OPEN position is on 0% | C.01: Put 50 and 100 % in OPEN position.; C.02: CFC is 50 % and 100% opened.
2 | CFC is in AUTO mode and setpoint is set. | C.01: Pressure in CFC rises.
CFC keeps desired setpoint.
3 | CFC Bypass valve is in MANUAL mode and closed. | C.01: Open the CFC Bypass valve.; C.02: CFC Bypass valve is opening.
4 | CFC Bypass valve is in AUTO mode and Bypass pressure difference is set. | C.01: Pressure from CFC drops below setpoint - Bypass pressure difference.; C.02: CFC Bypass valve is automatically opening.
Optional*
CAS Operational Data: | bar: C.01 to C.07
Shift | Working Compressors |  | Nm3/m | Hours | Shift Timing | Lunch Timing | Tea Break
1st
2nd
3rd
Products Manufactured:
Describe Point of Use of compressed air:
| Working Days / Year: | C.03: Weekly holiday on:
| Main Header Size : | C.02: mm ø; C.04: Length :; C.07: m
Receiver Capacity: | bar: C.01 to C.02
Dryer: |  | C.02: Type:; C.03: Refrigeration/ Heatless Regenerative/ Heated Regenerative/ HOC
Make: |  | C.02: Capacity:; C.04: m3/m; C.05: Dp across Dryer:; C.07: bar
● Do you have any specific problem at your compressed air system, that needs a solution?
● Please draw a single line schematic diagram of your Compressed Air system along with this data sheet.
Process diagram of compressed air system (production-distribution-users): DN PN pipelines (or actual PI&D copy)
| Test results | C.01: Comply; C.02: Not comply
kWh/m3
kW/m3/min
kW/100cfm
kW/cfm
barg
kPa
PSI
barg
kPa
PSI
barg
kPa
PSI
barg
kPa
PSI
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No
Yes/No

## EMCS
CAEMS CS-2-4-8-CFC Field Installation Setup IQ-OQ EMCS Settings
Pressure: |  |  |  | Timers:
Pressure Setpoint |  |  | barg | NORMAL START |  |  | sec
Pressure Setpoint offset |  |  | barg | CRITICAL START |  |  | sec
Min Critical Pressure |  |  | barg | Load/Unload |  |  | sec
Max. Critical Pressure |  |  | barg | Unload Stop(long) |  |  | sec
EMCS Pressure Analog input: |  |  | barg | Unload Stop(short) |  |  | sec
Advanced Settings: |  |  |  | Control Mode:
Start 2nd compressor |  |  |  | Priorities:
VSD Reserved Power |  |  |  | Energy Mode:
Enable Auto Stopping Priorities |  |  |  | Schedules:
PRIORITY SETTINGS:
Prim.Starting prio. |  |  | Prim. Stopping prio. |  |  | Priority switching active:
Sec.Starting prio. |  |  | Sec. Stopping prio.
|  |  | Switching priorities every |  |  |  | hours
ENERGY MODE SETTINGS:
Average flow to: |  |  |  | Starting prio. |  | Stoping prio.
1. |  | m3/min
2. |  | m3/min
3. |  | m3/min
Flow ave. Time calc.:
hours
SCHEDULES 1:
| Start Day | HOUR | MIN | Starting prio. | Stopping prio |  | ENABLE
1.
2.
3.
SCHEDULES 2:
| Start Day | HOUR | MIN | Starting prio. | Stopping prio |  | ENABLE
4.
5.
6.
SCHEDULES 3:
| Start Day | HOUR | MIN | Starting prio. | Stopping prio |  | ENABLE
7.
8.
9.
StopStart Function:
StopStart Function |  |  | Start/stop schedule
Pressure Tanks Capacity |  |  | m3
Prefill time |  |  | min
Stop/Start Schedule setup:
Start at: |  | HOUR : MIN | Stop at: | HOUR : MIN
Monday
Tuesday
Wednesday
Thursday
Friday
Saturday
Sunday
ON/OFF
ON/OFF
ON/OFF
ON/OFF
ON/OFF
ON/OFF
ENABLE/DISABLE
ENABLE/DISABLE
ENABLE/DISABLE
ENABLE/DISABLE
ENABLE/DISABLE
ENABLE/DISABLE
ENABLE/DISABLE
ENABLE/DISABLE
ENABLE/DISABLE
ENABLE/DISABLE
ENABLE/DISABLE
ENABLE/DISABLE

## CFC
CAEMS CS-2-4-8-CFC Field Installation Setup IQ-OQ CFC Settings
CFC Settings |  |  | PID parameters: MRV1
CFC Flowcontroller |  |  | Pb |  | sec | PID Max | %
BRV1 |  |  | Ti |  | sec | PID Min | %
CFC Function |  |  | Td |  | sec | Open/close Ramp | min
CFC Default Setpoint |  | barg | Damping |  | sec
BRV1 Open Difference |  | barg | Deadband |  | sec
CFC General Settings |  |  | PID parameters: BRV1
Empty System Function |  |  | Pb |  | sec | PID Max | %
CFC Inlet Pressure on AI |  |  | Ti |  | sec | PID Min | %
CFC Outlet Pressure on AI |  |  | Td |  | sec | PID Setpoint | %
CFC Off |  | barg | Damping |  | sec
|  |  | Deadband |  | sec
DI Setpoint |  | CFC Schedule
|  |  | Start Hour | Start Min | Setpoint
Predefined Setpoints |  | Monday SP1
Monday SP2
DI 6 | barg | Tuesday SP1
Tuesday SP2
DI 7 | barg | Wednesday SP1
Wednesday SP2
DI 8 | barg | Thursday SP1
Thursday SP2
Friday SP1
Friday SP2
Saturday SP1
Saturday SP2
Sunday SP1
Sunday SP2
AUTO
MANUAL
AUTO
MANUAL
No function
DI Setpoint
CFC Schedule

## Shut Off Valves
CAEMS CS-2-4-8-CFC Field Installation Setup IQ-OQ SOV Settings
SOV 1 Schedule
SOV Settings |  |  |  |  | Open Hour : Min | Close Hour : Min
| Name |  |  | Monday
SOV1 |  |  |  | Tuesday
Wednesday
SOV2 |  |  |  | Thursday
Friday
SOV3 |  |  |  | Saturday
Sunday
SOV 2 Schedule |  |  |  | SOV 3 Schedule
| Open Hour : Min | Close Hour : Min |  |  | Open Hour : Min | Close Hour : Min
Monday |  |  |  | Monday
Tuesday |  |  |  | Tuesday
Wednesday |  |  |  | Wednesday
Thursday |  |  |  | Thursday
Friday |  |  |  | Friday
Saturday |  |  |  | Saturday
Sunday |  |  |  | Sunday
AUTO
MANUAL
AUTO
MANUAL
AUTO
MANUAL

## 3. IQ - OQ Test Procedures Spec
CAEMS CS-4 IQ-OQ Test Procedures Specification
1 | IQ OQ PLC – Input/output signal and wiring test
1.1 Test purpose
The purpose of the IQ-OQ test is to test input / output signals on the controller (PLC) and to verify the compliance of the electrical connections. This involves visually checking the effect signal to the process actuators and meassuring equipment (e.g. Compressors, Pressure transmitters, flow meters ...)
1.2 Necessary equipment and conditions for carrying out the tests.
1. Test participants should be familiar with the object. They must know the electro and mechanical part of the system.
2. Tests are carried out by electrician that is familiar with the system and is supervised by customer.
2. Required equipment : Current supply simulator, multimeter and laptop with valid PLC software installed.
1.3 Test procedure
1.3.1 Start PLC program
PLC program download to PLC and start it. PLC goes to RUN. When program is running we are able to simulate all the input/output signals.
1.3.2 Testing of analog intput settings
We have to check if wiring is made correctly. We also check if all sensors are installed correctly. With current simulator we simulate mA. We do three tests: 4mA, 12mA, 20mA. On computer we check if actual value complies with sent mA signal.
1.3.3 Testing of analog output settings
We have to check if wiring is made correctly. We also check if all actuators are installed correctly. From computer we simulate analog output: 0%, 50% and 100%. With ampermeter we measure signal mA.
1.3.4 Testing of input digital signals
We have to check if wiring is made correctly. We also check if all sensors are installed correctly. We also have to check if input is NO or NC. Then we check if signal is normaly recognized by PLC.
1.3.5 Testing of output digital signals
We have to check if wiring is made correctly. We also check if all sensors are installed correctly. On PLC we force output and check if signal is recognized by actuator ( compressor load valve,...).
2. | IQ HDS – CAEMS System Hardware Test
2.1 Test purpose
Purpose of this test is to confirm that hardware (PLC modules, communication modules,...) is installed properly and complies with HDS document specification.
2.2 Necessary equipment and conditions for carrying out the tests.
2.2.1. Test participants should be familiar with the object. They must know the electro, mechanical and measurement equipment of CAEMS.
2.2.2 Tests are carried out by electrician that is familiar with the system and is supervised by customer. For testing purpose we need HDS document specification.
2.3 Test procedure
1.1 Starting test procedure
Test is carried out by checking every location of installed modules ( CS-4 base unit, CS-VSD and CS-ON/OFF modules).
1.2 Visual checking
First we visually check all lights and equipment. On PLC and IO modules should light green LED. We also check if all measurement equipment is installed properly and there is no visual errors on it.
3. | IQ TAB HMI PLC – HMI Data test
3.1 Test purpose
Purpose of the test is to check if all signals are correctly transfered from PLC to HMI.
3.2 Necessary equipment and conditions for carrying out the tests.
3.2.1. Test participants should be familiar with the object. They must know the meaning of the each signal and know how to simulate it. They must know how to handle with HMI.
3.3 Test procedure
3.3.1. Starting test procedure
IQ TAB HMI test is carried out by checking signals compliance between PLC and HMI.
4. | IQ SDS – CAEMS Cloud System Application test
4.1 Test purpose
Test purpose is to check that CAEMS application is properly set up, all signals are live and online. We also check OpenVPN remote connection.
4.2 Necessary equipment and conditions for carrying out the tests.
4.2.1. Test participants should be familiar with the object. They must also be familiar with CAEMS web application and know how to setup it correctly.
4.2.2. Required equipment: computer with internet connection to CAEMS and installed OpenVPN.
4.3 Test procedure
1.1 Starting test procedure
In CAEMS we go to SETUP and check that all data (sensor ranges, calculations, compressor data,...) are typed correctly.
5 | OQ FNS PLC – CAEMS Control system Function Test
5.1 Test purpose
Purpose of this test is to check if all control functions work properly. We have to check all functions that are ordered from customer.
5.2 Necessary equipment and conditions for carrying out the tests.
5.2.1. Test participants should be familiar with the object. They must be familiar with PLC control functions and know how to simulate all possible options.
5.2.2. Test is carried out when all compressors are ready and available for remote control.
5.2.3. Required equipment: Currenty supply simulator, valid PLC software, HMI.
5.3 Test procedure
5.3.1 Starting procedure
Download PLC program to PLC and RUN the program.
We connect computer to PLC and check all control functions by simulating possible pressure, flow conditions.
6 | Final compliance checking
Test | Description | Test COMPLIES (Yes, No) | Signature 1 | Signature 2 | Date | Remarks
IQ-OQ PLC | Input/output analog and digital signals testing
HDS | Hardware specification document compliance
IQ TAB HMI-PLC | HMI-PLC signals compliance
SDS | CAEMS web application compliance
FNS | Control functions compliance

## 4. CAS specific questions
| Compressor Installation Specific. | Company specifics
1 | How old is this compressor? How many hours will the compressor run ?
2 | What is the average air consumption?
3 | What is your electrical unit cost?
4 | Does it change for day shift / night shift?
5 | What is the plant minimum pressure?
6 | What is the existing pressure band Minimum / Maximum / Useful Differential?
7 | Are there several compressors running together?
8 | How are they controlled?
9 | What ancillaries are fitted (dryers, filters)?
10 | What is the pressure drop Initial & at element change?
11 | What is the size of there pipe work?
12 | What is the pressure drop they have?
Compressed Air System Specific.
1 | What do you think the min pressure is?
2 | Is there a piece of production equipment that needs a higher pressure than the majority of the plant?
3 | Do you have pressure drop?
4 | Do you know size of piping distribution ?
5 | Are you happy with current service supplier who is currently doing this work ?
6 | Do you have production problems ?
7 | How reliable is your existing system?
8 | Do you have air quality issues and if yes what happens?
9 | How much do you pay for electricity ?
10 | Do you know how efficient your compressed air systém is ?
11 | Working hours of airend
12 | Are you proactive in fixing leaks ?
13 | Do you have any unregulated air users ?
14 | What is your shift rotation and does demand change ?
15 | Do you isolate supply to non production areas ?
16 | Do you have a LP or HP air system ?
17 | Do you have a high failure rate of production equipment ?
18 | What happens when the pressure is too low ?
19 | Quality of air need and is this different for different air users ?
20 | Is there any large volume demand events but short duration?
21 | Do you have sufficient back up machines?
22 | What is the cost of lost production ?
23 | When was the last time you auditted the air system ?
25 | Are you or are you working to ISO 14001 ?
26 | Would you consider total air responsibility outsoucing?
27 | Pay as you use ?
28 | Air over the fence
29 | Why do you value your existing service / compressor provider ?
30 | Do you use hot water in your production process ?
31 | Do you have problems with corrosion in your pipe work,
32 | Is there any product spoilage?
33 | How much money does it cost per hour in lost production if your air fails?
34 | How much are you spending on equipment repairs due to moisture contamination?
35 | How much are your air leaks costing you?

## CALMS-CAEMS Users
CALMS / CAEMS application user table | [5 empty] | WWW.CALMS.COM
Company: |  |  | Company Logo:
CALMS ID: | [5 empty] | Date:
CAEMS ID:
Name | Surname | Email = Username | Language | Status | Manager report | Automatic reporting CALMS CAEMS | Can measure | Can analize | Can add CALMS | Can edit CALMS | Can delete CALMS | Can add location | Can add user | Can use CAEMS | Can add CAEMS | Can edit CAEMS | Can run analysis | Can acknowledge CAEMS alarms & warnings | Can add/edit/delete CAEMS events | Can DELETE complete CAEMS | Pressure unit | Flow unit | Curency
The above users are assigned by Customer to have access to CALMS / CAEMS web server application and they agreed with CALMS GENERAL CONDITIONS AGREEMENT AND POLICY OF DATA PROTECTION
Only users assigned by customer can have access to modify or delete all customer data from the server and backups.
By signing and using the CALMS server website, the users agrees to the CALMS general conditions agreement and Policy of Protecting of business data and accepts them.
| Customer signature: |  |  |  |  | Date: